EXISITNG BUILDING ENVIRONMENT CONDITIONS

| Item | Cooling | Notes |
| --- | --- | --- |
| Latitude | - | 3.57° N |
| Longitude | - | 98.67° E |
| Elevation |  | 25 m |
| Indoor temperature | 28°C |  |
| Indoor relative humidity | 65 % |  |
| Outdoor temperature | 34 °C |  |
| Outdoor Relative Humidity | 82%a |  |
| Wind Speed | 2 m/s |  |
| ∆T | 6 °C | T(outdoor-indoor) |
| Outdoor wet bulb temperature | 27 °C | MCWBb at 1% |

.a Climate Consultant 6.0 beta, IWEC data, IWEC=International Weather for Energy Calculations.

.b MCWB = Mean Coincident Wet Bulb

EXISTING BUILDING ENVELOPE AREA

| Component | Area (m2) | Notes |
| --- | --- | --- |
| Ceiling (Roof) | 375 |  |
| Doors | 23 | 3(0.9 x 2 m) , 1(2x2m), 1(1.8x2m), 1(5x2m) |
| Windows | 26.925 | 14(0.8x1.5m), 5(0.75x1m), 3(0.5x0.75m), 1(1.5x2m), 1(0.75x2m), 1(0.5x3m) |
| Outdoor walls | Gross=280, net=230.075 | Wall height = 3.5m |
| Slab Floor above grade | 375 | Unheated |

EXISTING BUILDING ENVELOPE PROPERTIES

| Assembly | Basic Construction | Thermal component | U-value W/(m2·K) | Insulation (m2·K)/W |
| --- | --- | --- | --- | --- |
| Outdoor Wall | Concrete masonry (150mm, 1840 kg/m3) | - | 2.63 | 0.23 |
| Celling (Roof) | Standard wood joists, single rafter | Gypsum board | 0.2 | 5.3 |
| (Slab) Floor | Unheated slab (150mm) | Concrete slab | F-1.264 | N/A |
| Doors | Swinging | Wood frames | 3.4 | N/A |
|  | Uninsulated double layer swinging | Metal frames | 4.0 | N/A |
| Windows | Clear & operable, Glazing Layer 1 | Wood frames | 5.05 | SHGC=0.64 |
| Construction | Average |  | Aula=2.8 cm2/m2 |  |

SHGC=Solar Heat Gain Coefficient

.a Unit leakage area

Source: ASHRAE 2013 fundamental, ASHRAE STANDARD 90.1.2007 (SI)

Rwall = without air film resistance

F =per linear foot of building perimeter

COOLING LOAD (SENSIBLE HEAT GAIN) THROUGH EXISTING BUILDING ENVELOPE

| Section | Net Area (m2) | U-value (W/m2 K) | CLTD (°C) | GLF | Cooling Load (W) |
| --- | --- | --- | --- | --- | --- |
| Roof | 375 | 0.2 | 23 |  | 1725 |
| South wall | 42.95a | 2.63 | 6 |  | 678 |
| North wall | 42.95a | 2.63 | 4 |  | 452 |
| East wall | 74.9a | 2.63 | 10 |  | 1970 |
| West wall | 84a | 2.63 | 10 |  | 2209 |
| South Doors | 4 | 4 | 6 |  | 96 |
| North Doors | 3.6 | 4 | 4 |  | 58 |
|  | 1.8 | 3.4 | 4 |  | 25 |
| East Doors | 3.6 | 3.4 | 10 |  | 122 |
| West Doors | - | N/A |  | N/A |  |
| South Windows | 5.55 | 5.05 |  | 85 | 472 |
| North Windows | 7.65 | 5.05 |  | 57 | 205 |
| East Windows | 9 | 5.05 |  | 142 | 1278 |
| West Windows | - | N/A |  | N/A |  |
| Infiltration | 15 |  |  | 2.2b | 33 |
| Total |  |  |  |  | 9323 |

.a Calculated from gross wall area less windows and doors areas

.b Infiltration factor, from the 1981 ASHRAE Handbook-Fundamental

CLTD = Cooling Load Temperature Differences

GLF = Glass Load Factor;

L (Low) applicable range: ∆T < 9 °C.

M (Medium) applicable range: 9 °C <∆T <14 °C

H (High) applicable range: ∆T > 14 °C

∆T= 2°C  L

Detailed calculation for cooling load (sensible heat gain) through existing building envelope:

- Gains through roof :

q = Uroof x A x CLTD

q = 0.2 x 375 x 23 = 1725 W

- Gains through walls :

q = Uwall x A x CLTD

South wall:

q = 2.63 x 42.95 x 6 = 677.75 W

North wall:

q = 2.63 x 42.95 x 4 = 451.84 W

East wall:

q = 2.63 x 74.9 x 10 = 1969.87 W

West wall:

q = 2.63 x 84 x 10 = 2209.2 W

- Gains through doors:

q = Udoor x A x CLTD

South doors:

q = 4 x 4 x 6 = 96 W

North doors:

q = 3.6 x 4 x 4 = 57.6 W

q = 1.8 x 3.4 x 4 = 24.48 W

East doors:

q = 3.6 x 3.4 x 10 = 122.4 W

- Gains through windows (using draperies):

q = A x GLF

South windows:

q = 5.55 x 85 = 471.75 W

North windows:

q = 3.6 x 57 = 205.2W

East windows:

q = 9 x 142 = 1278 W

- Gains from outdoor air

qinfiltration = Aexposed x infiltration factor

q = 15 x 2.2 = 33W

- Gains from people:

qpeople = number of occupant x sensible gain per occupant

q= 7 x 67 = 469 W

- Gains from equipment:

| Equipment Description | Average Power (W) |
| --- | --- |
| Desktop PC | 77 |
| 3 Laptop | 36 x 3 = 108 |
| 2 Flat panel monitor | 36 x 2 = 72 |
| 2 Printer | 74 x 2 = 148 |
| Water cooler | 350 |
| Oven | 645 |
| Toaster | 59 |
| Refrigerator | 4700 |
| 3 TV | 3 x 1000 = 3000 |
| Lighting | 7500 |

DESIGN NEW CONSRTUCTION BUILDING ENVELOPE PROPERTIES

| Assembly | Basic Construction | Thermal component | U-value W/(m2·K) | Insulation (m2·K)/W |
| --- | --- | --- | --- | --- |
| Outdoor Wall | Brick masonry (8cm, 1550 kg/m3) | Metal Stud | 0.16 | 6.4 |
| Indoor Wall | Laminated Veneer Lumber | Wood | 0.1 | 8.67 |
| Insulation | Fiberglass batt (9cm) |  | 0.01 | 11 |
| Celling | Standard wood joists, single rafter | Gypsum board | 0.25 | 3.9 |
| Roof | Asphalt | Wood fiber board | 0.2 | 4.7 |
| (Slab) Floor | Unheated slab (600mm) | Concrete slab | F-1.264 | N/A |
| Doors | Swinging | Wood frames | 2.2 | N/A |
|  | Uninsulated double layer swinging | Metal frames | 4.0 | N/A |
| Windows | Clear & operable, Glazing Layer 1 | Wood frames | 1.45 | SHGC=0.26 |
| Construction | Average |  | Aula=2.8 cm2/m2 |  |

SHGC=Solar Heat Gain Coefficient

.a Unit leakage area

Source: ASHRAE 2013 fundamental, ASHRAE STANDARD 90.1.2007 (SI)

PASSIVE COOLING SINGLE FAMILY RESIDENTIAL HOUSE IN INDONESIA

The design of residential building from the point of view building physics only for increasing the performance with naturally ventilated only.  So later on the HVAC mechanical cooling demand could be minimize in term of energy uses.

Here the pictures of the building design in 3D and 2D model draw with Autodesk Revit 2015 full version and energy analysis web based software Green Building Studio (www.gbs.autodesk.com) which embed with the Revit 2015 itself by using free trial account in 30 days.

House with roof view in 3D

House with ceiling view in 3D

House with interior view in 3D

House with side (East) view in 3D

House with side (West) view in 3D

House with side (West) view in 3D

House with Front (South) view in 3D

House with Rear (North) view in 3D

House with Floor Plan view in 2D

House with top view in 3D

House with front elevation view in 3D

Below are the schedules of the building assemblies:

The Sun Path.

The house is located in Medan, North Sumatera, Indonesia.

Latitude: 3.58

Longitude: 98.67

Elevation: 25m

Weather station distance from the house is around 7 km nearby.

Station name: Medan/Polonia (MIL)

World Meteorological Organization number: 960350

Elevation : 25 m

Standard pressure at station elevation: 101.03 KPa

Hours: + 7.00 UTC

Latitude: 3.57

Longitude: 98.68

The orientation of the house in global position with cast shadows appearance:

Sun Position at 12 pm local time, April 19 2015

Sun Position at 3 pm local time, April 19 2015

Sun Position at 9 am local time, April 19 2015

HVAC zone

The central active mechanical cooling will only installed inside some room parts of the house, such as all bedrooms, living room, and family room (hall). The rest of room such as bathrooms, kitchen will be hanged on ambient condition or just using exhaust cooling.

HVAC zone inside house